## Master
UoW Electrical Team - Infrastructure Supply Charateristics
|  |  |  | Supply Charateristics & Earthing Arrangements | [7 empty] | Particulars of Installation Origin | [8 empty] | Earthing and Protective Bonding Conductors | [5 empty] | Protective Bonding Conductors
Building code | Complete Y/N | Building | Last Updated | Earthing Arrangement | Number of Live Conductors | Type | Prospective Fault Current - Ipf (KA) | External earth Fault impedance - Ze | Supply Protective Device BS EN | Rated Current | Short Circuit Capacity | Means of Earthing | Maximum Demand | Protective Measure | Main Switch- BS EN | Rating - A | Suuply Conductor Material | CSA (mm) | RCD Main Switch - !n | Measured Operating Time | Earthing Conductor Material | CSA (mm) | Continuity Verified | Main Protective Bonding Material | CSA | Continuity Verified | Water | Gas | Lightning | Oil | Structural Steelwork | Other
3.036 | Y | Arden House | 2020-08-21 | TN-S | 3 Phase 4 wire | AC | 12.04 | 0.05 | BS 88 - 2 type Gg | 400 | 80 | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 400 | Copper | N/V | N/A |  | Copper | 120 | Yes | Copper | 50 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.177 | Y | A.M.M.C. | 2020-08-21 | TN-C-S | 3 Phase 4 wire | AC | 4.4 | 0.12 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 125 | Copper | 35 | N/A |  | Copper | 35 | Yes | Copper | 10 | Yes | Yes | N/A | N/A | N/A | N/A | N/A
1.063 | Y | Argent Court | 2020-08-21 | TN-C-S | 3 Phase 4 wire | AC | 19.8 | 0.02 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 600 | Copper | 300 | N/A |  | Copper | 150 | Lim | Copper | 25 | Lim | Yes | Yes | N/A | N/A | N/A | N/A
1.239 | Y | Argent Court North Annexe | 2020-08-21 | TN-C-S | 3 Phase 4 wire | AC | 3.02 | 0.15 | LIM | LIM |  | Distributors facility | N/V | ADS | BS 5419 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.26 | Y | Argent Court Data Centre - South Annexe | 2020-08-21 | TN-C-S | 3 Phase 4 wire | AC | 19.9 | 0.01 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 ACB | 2500 | Copper | 240 | N/A |  | Copper | 185 x 2 | Yes |  |  | N/V | N/V | N/V | N/V | N/V | N/V | N/V
1.217 | Y | Arthur Vick - 1 | 2020-08-21 | TN-S | 3 Phase 4 wire | AC | 15 | 0.03 | LIM | LIM |  | Distributors facility | N/V | ADS | BS4752 | 400 | Copper | 185 | N/A |  | Copper | 95 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
1.218 | Y | Arthur Vick - 2 | 2020-08-21 | TN-S | 3 Phase 4 wire | AC | 15 | 0.03 | LIM | LIM |  | Distributors facility | N/V | ADS | BS4752 | 400 | Copper | 185 | N/A |  | Copper | 95 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
1.219 | Y | Arthur Vick - 3 | 2020-08-21 | TN-S | 3 Phase 4 wire | AC | 15 | 0.03 | BS EN 60947 - 2 MCCB | 1600 | 65 | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 400 | Copper | 300 | N/A |  | Copper | 500 x 2 | Yes | Copper | 300 | Yes | N/A | N/A | N/A | N/A | Yes | N/A
1.001 | Y | Arts Centre | 2020-08-21 | TN-S | 3 Phase 4 wire | AC | 19.9 | 0.01 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 1600 | Copper | 300 x 2 | N/A |  | Copper | 120 x 2 | Yes | Copper | 95 x 2 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
3.001 | Y | Avon | 2020-08-21 | TN-C-S | 3 Phase 4 wire | AC | 7.4 | 0.08 | LIM | LIM |  | Distributors facility | N/V | ADS | BS 5419 | 160 | Copper | 70 | N/A |  | Steel | Armour | Yes | Copper | 10 | N/V | N/V | N/V | N/V | N/V | N/V | N/V
9.002 | N | Barford Boat House | 2020-08-21 | [10 empty] | ADS
3.024 | Y | Bericote | 2020-08-21 | TN-S | 3 Phase 4 wire | AC | 6.4 | 0.07 | BS 88 - 2 type Gg | 100 | 80 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 250 | Copper | 95 | N/A |  | Steel | 147 Armour | Yes | Copper | 25 | Yes | Yes | Yes | N/A | N/A | N/A | Yes
3.035 | N | Bericote Garages | 2020-08-21 | [10 empty] | ADS
16.002 | Y | The Bee Hive | 2020-08-21 | TN-S | 3 Phase 4 wire | AC | 4.98 | 0.09 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 800 | Copper | 185 x 2 | N/A |  | Copper | 185 | Yes | Copper | 25 | Yes | N/V | Yes | N/A | N/A | N/A
1.014 | Y | Benefactors Hall | 2020-08-21 | TN-S | 3 Phase 4 wire | AC | 5.2 | 0.11 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 400 | Copper | 120 | N/A |  | Copper | 70 | Yes | Copper | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V
2.005 | Y | Bio-Medical Research Institute (Life science) | 2020-08-21 | TN-S | 3 Phase 4 wire | AC | 8.46 | 0.05 | BS 88 - 2 type Gg | 400 | 80 | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 400 | Copper | 120 x 2 | N/A |  | Copper | 70 | Yes | Copper | 50 | Yes | Yes | Yes | N/A | N/A | N/V | N/A
2.006 | Y | Biotechnology (Bioscience) | 2020-08-21 | TN-C-S | 3 Phase 4 wire | AC | 6.8 | 0.06 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 2500 | Copper | 50 x 4 | N/A |  | Copper | 500 | Yes | Copper | 95 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
2.009 | Y | Biotechnology (Bioscience) Phase - 4 | 2020-08-21 | TN-S | 3 Phase 4 wire | AC | 13.86 | 0.04 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 400 | Copper | 120 x 2 | N/A |  | Copper | 95 | Yes | Copper | 50 | Yes | Yes | Yes | N/A | N/A | Yes | N/A
1.278 | Y | Bluebell - 1 | 2020-08-23 | TN-S | 3 Phase 4 wire | AC | 4.82 | 0.08 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 400 | Copper | 185 | N/A |  | Copper | 95 | Lim | Copper | 16 | Lim | Yes | N/A | Yes | N/A | N/A | N/A
1.279 | Y | Bluebell - 2 | 2020-08-23 | TN-S | 3 Phase 4 wire | AC | 16.2 | 0.02 | BS EN 60947 - 2 MCCB | 300 | 36 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 400 | Copper | 185 | N/A |  | Copper | 185 | Yes | Copper | 16 | Yes | Yes | N/A | Yes | N/A | N/A | Yes
1.28 | Y | Bluebell - 3 | 2020-08-23 | TN-S | 3 Phase 4 wire | AC | 4.4 | 0.04 | BS EN 60947 - 2 MCCB | 300 | 36 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 400 | Copper | 240 | N/A |  | Copper | 240 | Yes | Copper | 16 | Yes | Yes | N/A | Yes | N/A | Yes | Yes
1.281 | Y | Bluebell - 4 | 2020-08-23 | TN-S | 3 Phase 4 wire | AC | 17.3 | 0.04 | BS EN 60947 - 2 MCCB | 300 | 36 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 400 | Copper | 240 | N/A |  | Copper | 240 | Yes | Copper | 16 | Yes | Yes | N/A | Yes | N/A | Yes | Yes
1.282 | Y | Bluebell Wardens E | 2020-08-23 | TN-S | 3 Phase 4 wire | AC | 2.98 | 0.15 | BS EN 60947 - 2 MCCB | 63 | 36 | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 63 | Copper | 35 | N/A |  | Copper | 25 | Yes | Copper | 16 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.283 | Y | Bluebell Wardens F | 2020-08-23 | TN-S | 3 Phase 4 wire | AC | 2.7 | 0.16 | BS EN 60947 - 2 MCCB | 63 | 36 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Steel | Armour | Yes | Copper | 16 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.066 | Y | Boiler House | 2020-08-23 | TN-S | 3 Phase 4 wire | AC | 3.62 | 0.06 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 ACB | LIM | Copper | 300 x 2 | N/A |  | Copper | 95 | Yes | Copper | 35 x 2 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.037 | Y | Battery Abuse Centre | 2020-08-24 | TN-S | 3 Phase 4 wire | AC | 3.78 | 0.09 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 ACB | 1600 | Copper | Busbar | N/A |  | Copper | Tape 25 x 2.5 | Yes | Copper | 50 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.241 | Y | Battery Vibration Testing Centre | 2020-08-24 | TN-C-S | 3 Phase 4 wire | AC | 19 | 0.02 | BS EN 60947 - 2 ACB | 3200 | 65 | Distributors facility | 3200 | ADS | BS EN 60947 - 2 ACB | 3200 | Copper | 240 x 2 | N/A |  | Copper | 120 | Yes | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V
1.403 | N | Battery Abuse Centre Kiosk | 2020-08-24 | [10 empty] | ADS
1.419 | N | Battery Energy Storage | 2020-08-24 | [10 empty] | ADS
1.399 | N | BatteryTesting Unit | 2020-08-24 | [10 empty] | ADS
1.369 | N | Battery Storage Container | 2020-08-24 | [10 empty] | ADS
2.017 | Y | Car Park- 1 Gibbet Hill (D.B.) | 2020-08-24 | TN-C-S | 3 Phase 4 wire | AC | 0.76 | 0.3 | BS EN 60947 - 2 MCCB | 63 | 33 | Distributors facility | 100 | ADS | BS EN 60947 - 2 MCCB | 63 | Copper | 50 | N/A |  | Copper | 10 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
2.018 | Y | Car Park-1 A . (Gibbet Hill) | 2020-08-24 | TN-S | 3 Phase 4 wire | AC | 5.68 | 0.08 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 250 | Copper | 50 x 2 | N/A |  | Copper | 95 | Lim | Copper | 25 | Lim | N/A | N/A | N/A | N/A | N/A | N/A
2.019 | N | Car Park-1 B . (Gibbet Hill) Medical | 2020-08-24 | [10 empty] | ADS
2.02 | N | Car Park-1 C (Gibbet Hill C.T.U ) | 2020-08-24 | [10 empty] | ADS
1.085 | Y | Car Park - 2 (Behind Rootes Bluebell ) | 2020-08-24 | TN-S | 3 Phase 4 wire | AC | 5.18 | 0.09 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 125 | Copper | 25 | N/A |  | Steel | Armour | Lim | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1.086 | N | Car Park - 3 Cryfield | 2020-08-24 | [10 empty] | ADS
1.087-1.088 | N | Car Park 4+5 Now Bus Interchange | 2020-08-25 | [10 empty] | ADS
1.089 | N | Car Park - 6 | 2020-08-25 | [10 empty] | ADS
1.091 | Y | Car Park - 8 (Opp Sports Centre) | 2020-08-25 | TN-S | 3 Phase 4 wire | AC | 3.06 | 0.15 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 250 | Copper | 35 | N/A |  | Steel | Armour | Lim | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1.092 | N | Car Park - 8A (D.B.) | 2020-08-25 | [10 empty] | ADS
1.093 | N | Car Park - 9 (D.B.) | 2020-08-25 | [10 empty] | ADS
1.094 | N | Car Park - 10 | 2020-08-25 | [10 empty] | ADS
1.095 | N | Car Park - 10A | 2020-08-25 | [10 empty] | ADS
1.096 | N | Car Park 10B | 2020-08-25 | [10 empty] | ADS
1.097 | N | Car Park - 11 | 2020-08-25 | [10 empty] | ADS
3.038 | Y | Car Park - 12 | 2020-08-25 | TN-S | 3 Phase 4 wire | AC | 0.53 | 0.42 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 125 | Copper | 10 | N/A |  | Steel | Armour | Lim | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
3.04O | Y | Car Park - 13 (adj Warwick Sports) | 2020-08-25 | TN-S | 3 Phase 4 wire | AC | 0.5 | 0.48 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 10 | N/A |  | Steel | Armour | Lim | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
3.041 | Y | Car Park - 14 Westwood (D.B.) | 2020-08-25 | TN-S | 3 Phase 4 wire | AC | 3.86 | 0.11 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 160 | Copper | 95 | N/A |  | Copper | LIM | Lim | Cooper | LIM | N/V | Yes | N/A | Yes | N/A | Yes | N/A
3.082 | N | Car Park - 14A | 2020-08-25 | [10 empty] | ADS
1.098 | Y | Car Park - 15. (Opp. Rear of W.M.G.) (D.B.) | 2020-08-25 | TN-S | 3 Phase 4 wire | AC | 2.36 | 0.19 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 250 | Copper | 35 | N/A |  | Steel | Armour | Lim | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1.099 | Y | Car Park - 16. (Front Of University House.) (D.B.) | 2020-08-25 | TN-S | 3 Phase 4 wire | AC | N/A | N/A | LIM | LIM |  | Distributors facility | N/V | ADS
1.1 | N | Car Park - 17.(Rear of University House) | 2020-08-26 | [10 empty] | ADS
1.101 | N | Car Park - Scarman House | 2020-08-26 | [10 empty] | ADS
1.103 | N | Car Park - Heronbank Apartments | 2020-08-26 | [10 empty] | ADS
1.104 | N | Car Park Heronbank Loading Bay | 2020-08-26 | [10 empty] | ADS
1.105 | N | Car Park - Heronbank | 2020-08-26 | [10 empty] | ADS
1.106 | N | Car Park - Lakeside Apartments | 2020-08-26 | [10 empty] | ADS
1.107 | N | Car Park - Lakeside | 2020-08-26 | [10 empty] | ADS
1.114 | N | Car Park - Cryfield Cottages | 2020-08-26 | [10 empty] | ADS
1.413 | N | Car Park - Cryfield Old Farmhouse | 2020-08-26 | [10 empty] | ADS
1.111 | N | Car Park - Cryfield Pavillion | 2020-08-26 | [10 empty] | ADS
1.108 | N | Car Park - Cryfield Road | 2020-08-26 | [10 empty] | ADS
1.044 | N | Car Park - Physics Loading Bay | 2020-08-26 | [10 empty] | ADS
1.113 | N | Car Park Physical Science | 2020-08-26 | [10 empty] | ADS
1.262 | N | Car Park - Milburn House | 2020-08-26 | [10 empty] | ADS
1.109 | N | Car Park - Milking Parlour | 2020-08-26 | [10 empty] | ADS
1.11 | N | Car Park - Health Centre | 2020-08-26 | [10 empty] | ADS
1..275 | N | Car Park - Health Centre Road | 2020-08-26 | [10 empty] | ADS
1.112 | N | Car Park - Arts Centre (Rear) | 2020-08-26 | [10 empty] | ADS
1.115 | N | Car Park - Rear Of Library | 2020-08-26 | [10 empty] | ADS
1.116 | N | Car Park - Computer Science | 2020-08-26 | [10 empty] | ADS
1.117 | N | Car Park - I.A.R.C. | 2020-08-26 | [10 empty] | ADS
1.41 | N | Car Park - I.A.R.C. Delivery Yard | 2020-08-26 | [10 empty] | ADS
1.118 | N | Car Park - Zeeman Building | 2020-08-26 | [10 empty] | ADS
1.119 | N | Car Park - Rear of Senate House | 2020-08-26 | [10 empty] | ADS
1.12 | N | Car Park - Social Studies | 2020-08-26 | [10 empty] | ADS
1.121 | N | Car Park - Tocil Warden | 2020-08-26 | [10 empty] | ADS
1.122 | N | Car Park - Arthur Vic L.B. | 2020-08-26 | [10 empty] | ADS
1.123 | N | Car Park - Clay croft | 2020-08-26 | [10 empty] | ADS
1.124 | N | Car Park - Jack Martin L.B. | 2020-08-26 | [10 empty] | ADS
1.125 | N | Car Park Humanities | 2020-08-26 | [10 empty] | ADS
1.298 | Y | Car Park - Lynchgate (D.B.) | 2020-08-26 | TN-C-S | 3 Phase 4 wire | AC | 2.28 | 0.11 | BS EN 60947 - 3 | 250 |  | Distributors facility | 250 | ADS | BS EN 60947 - 3 | 250 | Copper | 185 | N/A |  | Copper | 70 | Yes | Copper | 50 | Yes | N/A | N/A | Yes | N/A | Yes | N/A
1.126 | N | Car Park - I.M.C. | 2020-08-26 | [10 empty] | ADS
1.402 | N | Car Park - A.A.M.C. Yard | 2020-08-26 | [10 empty] | ADS
3.039 | N | Car Park - Arden House | 2020-08-26 | [10 empty] | ADS
1.263 | N | Car Park - Argent Court | 2020-08-26 | [10 empty] | ADS
3.042 | N | Car Park - Avon | 2020-08-26 | [10 empty] | ADS
3.044 | N | Car Park - Life Long Learning. | 2020-08-26 | [10 empty] | ADS
2.037 | N | Car Park - Gibbet Hill Multi Storey | 2020-08-26 | [10 empty] | ADS
1.409 | Y | Car Park - I.P.S.I. Delivery Yard | 2020-08-26 | TN-C-S | 3 Phase 4 wire | AC | 2.26 | 0.11 | BS EN 60947 - 3 | 250 |  | Distributors facility | 250 | ADS | BS EN 60947 - 3 | 250 | Copper | 185 | N/A |  | Copper | 70 | Yes | Copper | 50 | Yes | N/A | N/A | Yes | N/A | Yes | N/A
3.083 | N | Car Park - I.T.S. Delivery Yard | 2020-08-26 | [10 empty] | ADS
1.416 | N | Car Park - Kirby Corner | 2020-08-26 | [10 empty] | ADS
1.38 | N | Car Park - Radcliffe House | 2020-08-26 | [10 empty] | ADS
1.261 | N | Car Park - Rootes D Service | 2020-08-27 | [10 empty] | ADS
1.412 | N | Car Park - Rootes Grocery | 2020-08-27 | [10 empty] | ADS
1.264 | N | Car Park - W.B.S. | 2020-08-27 | [10 empty] | ADS
3.043 | N | Car Park - Westwood Laundry | 2020-08-27 | [10 empty] | ADS
3.046 | N | Car Park - Westwood Loxley | 2020-08-27 | [10 empty] | ADS
3.045 | N | Car Park - Westwood Old Pool | 2020-08-27 | [10 empty] | ADS
3.048 | N | Car Park - Westwood Precincts | 2020-08-27 | [10 empty] | ADS
3.047 | N | Car Park - Willow Lodge | 2020-08-27 | [10 empty] | ADS
3.011 | Y | Continuing Education (Centre for L.l. Learning) learning | 2020-08-26 | TN-C-S | 3 Phase 4 wire | AC | 13.1 | 0.13 | LIM | LIM |  | Distributors facility | N/V | ADS | BS 5419 | 100 | Copper | 35 | N/A |  | Copper | LIM | Lim | Copper | LIM | Lim | Yes | Yes | N/A | N/A | N/A | N/A
1.021 | Y | Chaplaincy | 2020-08-26 | TN-S | 3 Phase 4 wire | AC | 4.3 | 0.06 | LIM | LIM |  | Distributors facility | N/V | ADS | LIM | LIM | Copper | 300 | N/A |  | Copper | 120 | Lim | Copper | 35 | Lim | Yes | N/A | N/A | N/A | N/A | N/A
1.365 | N | Chiller Farm | 2020-08-26 | [10 empty] | ADS
1.19O | Y | Claycroft - 1 | 2020-08-26 | TN-C-S | 3 Phase 4 wire | AC | 4.8 | 0.09 | BS EN 60947 - 2 MCCB | 650 | 36 | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 650 | Copper | 185 x 2 | N/A |  | Copper | 185 | Yes | Copper | 95 | Yes | Yes | Yes | N/A | N/A | Yes | N/A
1.191 | Y | Claycroft 2 | 2020-08-26 | TN-S | 3 Phase 4 wire | AC | 5.74 | 0.07 | LIM | LIM |  | Distributors facility | N/V | ADS | IEC 157-1 | 1000 | Copper | 300 x 2 | N/A |  | Copper | 120 | Yes | Copper | 95 | Yes | Yes | N/A | N/A | N/A | N/A | N/A
1.192 | Y | Claycroft - 3 | 2020-08-26 | TN-S | 3 Phase 4 wire | AC | 3.74 | 0.07 | LIM | LIM |  | Distributors facility | N/V | ADS | IEC 157-1 | 1000 | Copper | 300 x 2 | N/A |  | Copper | 120 | Yes | Copper | 95 | Yes | Yes | N/A | N/A | N/A | N/A | N/A
2.025 | Y | Clinical Trials Unit | 2020-08-26 | TN-S | 3 Phase 4 wire | AC | 9.68 | 0.05 | LIM | LIM |  | Distributors facility | N/V | ADS | BS 5419 | 400 | Copper | 150 X 2 | N/A |  | Copper | 95 | Yes | Copper | 50 | Yes | Yes | N/A | N/A | N/A | Yes | N/A
3.023 | Y | Compton | 2020-08-26 | TN-S | 3 Phase 4 wire | AC | 4.04 | 0.11 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 250 | Copper | 95 | N/A |  | Copper | Armour | Lim | Copper | 25 | Lim | Yes | Yes | N/A | N/A | N/A | N/A
3.033 | N | Compton Garages | 2020-08-26 | [10 empty] | ADS
1.008 | Y | Computer Science Building | 2020-09-01 | TN-S | 3 Phase 4 wire | AC | 4.4 | 0.04 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 1250 | Copper | 630 | N/A |  | Copper | 150 | Lim | Copper | 50 | Lim | Yes | Yes | Yes | N/A | N/A | N/A
1.077 | N | Computer Science Chiller | 2020-09-01 | [10 empty] | ADS
1.017 | Y | Coventry House (Senate House) | 2020-09-01 | TN-C-S | 3 Phase 4 wire | AC | 15 | 0.05 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 600 | Copper | 300 | N/A |  | Copper | 120 | Yes | Copper | 35 | Yes | Yes | N/A | N/A | N/A | Yes | Yes
1.062 | Y | Cryfield V.C.Barn+Outbuildings | 2020-09-01 | TN-S | 3 Phase 4 wire | AC | 2.88 | 0.27 | N/A | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Steel | Armour | Yes | Copper | 16 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
1.012 | Y | Cryfield Gardeners Compound | 2020-09-01 | TN-S | 3 Phase 4 wire | AC | 1.68 | 0.27 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 125 | Copper | 120 | N/A |  | Steel | Armour | Yes
1.06O | Y | Cryfield Grange Farm Garage & out buildings | 2020-09-01 | TN-S | 3 Phase 4 wire | AC | 2.88 | 0.27 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Steel | Armour | Yes | Copper | 16 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
1.061 | Y | Cryfield New Farmhouse (Wardens) | 2020-09-01 | TN-S | 3 Phase 4 wire | AC | 0.71 | 0.32 | LIM | LIM |  | Distributors facility | N/V | ADS | BS 5419 | 100 | Copper | 16 | N/A |  | Copper | 16 | Lim | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.024 | Y | Cryfield Old Farmhouse (Vice chancelors Ho.) | 2020-09-01 | TN-S | 3 Phase 4 wire | AC | 3.99 | 0.21 | LIM | LIM |  | Distributors facility | N/V | ADS | MCCB Obsolete | 250 | Copper | 150 | N/A |  | Steel | Armour | Lim | Copper | 16 | Lim | Yes | Yes | N/A | N/A | N/A | N/A
1.257 | Y | Cryfield Compound Shed | 2020-09-02 | TT | 3 Phase 4 wire | AC | N/A | N/A | N/A | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 125 | Copper | 35 | N/A | ? | Copper | 16 | Lim | Copper | N/V | Lim | N/A | N/A | N/A | N/A | N/A | N/A
1.059 | Y | Cryfield Grange Farm | 2020-09-02 | TN-S | 3 Phase 4 wire | AC | 4.1 | 0.22 | LIM | LIM |  | Distributors facility | N/V | ADS | MCCB Obsolete | 250 | Copper | 120 | N/A |  | Copper | 50 | Yes | Copper | 16 | Yes | Yes | Yes | N/A | N/A | Yes | N/A
1.026 | Y | Cryfield Milking Parlour | 2020-09-02 | TN-S | 3 Phase 4 wire | AC | 3 | 2.3 | LIM | LIM |  | Distributors facility | N/V | ADS | BS4752 | 250 | Copper | 120 | N/A |  | Copper | 95 | Yes | Copper | 10 | Yes | Yes | N/A | N/A | N/A | N/A | N/A
1.285 | N | Cryfield Barn - 1 | 2020-09-02 | [10 empty] | ADS
1.286 | N | Cryfield Barn - 2 | 2020-09-02 | [10 empty] | ADS
1.287 | N | Cryfield Barn - 3 | 2020-09-02 | [10 empty] | ADS
1.288 | N | Cryfield Barn - 4 | 2020-09-02 | [10 empty] | ADS
1.398 | N | Cryfield Hall - 0 | 2020-09-02 | [10 empty] | ADS
1.179 | Y | Cryfield Hall - 1 | 2020-09-02 | TN-S | 3 Phase 4 wire | AC | 6.67 | 0.06 | BS 88 - 2 type Gg | 200 |  | Distributors facility | 200 | ADS | BS EN 60947 - 2 MCCB | 200 | Copper | 120 | N/A |  | Copper | 70 | N/V | Copper | 50 | N/V | Yes | Yes | N/A | N/A | N/A | N/A
1.18O | Y | Cryfield Hall - 2 | 2020-09-02 | TN-S | 3 Phase 4 wire | AC | 4.08 | 0.11 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 1600 | Copper | 95 | N/A |  | Copper | 70 | Yes | Copper | 25 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.181 | Y | Cryfield Hall - 3 | 2020-09-02 | TN-S | 3 Phase 4 wire | AC | 7.9 | 0.06 | BS 88 - 2 type Gg | 200 |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 200 | Copper | 95 | N/A |  | Copper | 70 | N/V | Copper | 50 | N/V | Yes | Yes | N/A | N/A | N/A | N/A
1.385 | N | Cryfield Hall - 4 | 2020-09-02 | [10 empty] | ADS
1.386 | N | Cryfield Hall - 5 | 2020-09-02 | [10 empty] | ADS
1.387 | N | Cryfield Hall - 6 | 2020-09-02 | [10 empty] | ADS
1.388 | N | Cryfield Hall - 7 | 2020-09-02 | [10 empty] | ADS
1.389 | N | Cryfield Hall - 8 | 2020-09-02 | [10 empty] | ADS
1.39O | N | Cryfield Hall - 9 | 2020-09-02 | [10 empty] | ADS
1.391 | N | Cryfield Hall - 10 | 2020-09-02 | [10 empty] | ADS
1.392 | N | Cryfield Hall - 11 | 2020-09-02 | [10 empty] | ADS
1.393 | N | Cryfield Hall - 12 | 2020-09-02 | [10 empty] | ADS
1.394 | N | Cryfield Hall - 13 | 2020-09-02 | [10 empty] | ADS
1.395 | N | Cryfield Hall - 14 | 2020-09-02 | [10 empty] | ADS
1.396 | N | Cryfield Hall - 15 | 2020-09-02 | [10 empty] | ADS
1.397 | N | Cryfield Hall - 16 | 2020-09-02 | [10 empty] | ADS
1.136 | Y | Cryfield Cottage - 1 | 2020-09-02 | TN-C-S | 1 Phase 2 Wire | AC | 3.12 | 0.08 | BS 88 - 2 type Gg | 80 | 80 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.137 | Y | Cryfield Cottage - 2 | 2020-09-02 | TN-C-S | 1 Phase 2 Wire | AC | 1.14 | 0.02 | BS1361 - Type 1 | 80 | 33 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.138 | Y | Cryfield Cottage - 3 | 2020-09-02 | TN-C-S | 1 Phase 2 Wire | AC | 1.31 | 0.2 | BS1361 - Type 1 | 100 | 33 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.139 | Y | Cryfield Cottage - 4 | 2020-09-02 | TN-C-S | 1 Phase 2 Wire | AC | 1.08 | 0.21 | BS1361 - Type 1 | 100 | 33 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.14O | Y | Cryfield Cottage - 5 | 2020-09-02 | TN-C-S | 1 Phase 2 Wire | AC | 1.01 | 0.23 | BS1361 - Type 1 | 100 | 33 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.141 | Y | Cryfield Cottage - 6 | 2020-09-02 | TN-C-S | 1 Phase 2 Wire | AC | 0.97 | 0.24 | BS1361 - Type 1 | 100 | 33 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.142 | Y | Cryfield Cottage - 7 | 2020-09-02 | TN-C-S | 1 Phase 2 Wire | AC | 1.94 | 0.13 | BS1361 - Type 1 | 100 | 33 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.143 | Y | Cryfield Cottage - 8 | 2020-09-02 | TN-C-S | 1 Phase 2 Wire | AC | 0.66 | 0.36 | BS1361 - Type 1 | 100 | 33 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.144 | Y | Cryfield Cottage - 9 | 2020-09-02 | TN-C-S | 1 Phase 2 Wire | AC | N/V | 0.21 | BS1361 - Type 1 | 100 | 33 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.145 | Y | Cryfield Cottage - 10 | 2020-09-02 | TN-C-S | 1 Phase 2 Wire | AC | 0.87 | 0.27 | BS1361 - Type 1 | 100 | 33 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.146 | Y | Cryfield Cottage - 11 | 2020-09-02 | TN-C-S | 1 Phase 2 Wire | AC | 0.87 | 0.27 | BS1361 - Type 1 | 100 | 33 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.147 | Y | Cryfield Cottage - 12 | 2020-09-02 | TN-C-S | 1 Phase 2 Wire | AC | 0.96 | 0.24 | BS 88 - 2 type Gg | 63 | 80 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 16 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.148 | Y | Cryfield Cottage - 13 | 2020-09-02 | TN-C-S | 1 Phase 2 Wire | AC | 0.68 | 0.45 | BS1361 - Type 1 | 100 | 33 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.148 | Y | Cryfield Cottage - 14 | 2020-09-02 | TN-C-S | 1 Phase 2 Wire | AC | 0.68 | 0.45 | BS1361 - Type 1 | 100 | 33 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.169 | N | Cryfield Cricket Pavillion - 1 | 2020-09-02 | [10 empty] | ADS
1.17O | N | Cryfield Cricket Pavillion - 2 | 2020-09-02 | [10 empty] | ADS
1.377 | Y | Cryfield Energy Centre | 2020-09-03 | TN-S | 3 Phase 4 wire | AC | 3.8 | 0.13 | BS EN 60947 - 2 MCCB | 800 | 80 | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 800 | Copper | 630 | N/A |  | Copper | 630 | Yes | Copper | 25 | Yes | Yes | Yes | N/A | Yes | Yes | N/A
1.178 | N | Cryfield Energy Centre Gas House | 2020-09-03 | [10 empty] | ADS
1.254 | Y | Digital Laboratory | 2020-09-03 | TN-S | 3 Phase 4 wire | AC | 10.6 | 0.02 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 630 | Copper | 300 | N/A |  | Copper | 300 | Yes | Copper | 50 | Yes | Yes | N/A | N/A | N/A | Yes | N/A
3.022 | Y | Dunsmere | 2020-09-03 | TN-S | 3 Phase 4 wire | AC | 4.05 | 0.14 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 MCCB | 250 | Copper | 95 | N/A |  | Copper | 25 | Lim | Copper | 25 | Lim | Yes | Yes | N/A | N/A | N/A | N/A
3.032 | N | Dunsmere Garages | 2020-09-03 | [10 empty] | ADS
3.021 | Y | Emscote | 2020-09-03 | TN-S | 3 Phase 4 wire | AC | 6.4 | 0.07 | BS 88 - 2 type Gg | 100 | 80 | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 250 | Copper | 120 | N/A |  | Copper | Armour | Yes | Copper | 25 | Yes | Yes | Yes | N/A | N/A | Yes | N/A
3.016 | Y | Engineering Management Building (EMB) | 2020-09-03 | TN-S | 3 Phase 4 wire | AC | 3.7 | 0.09 | LIM | LIM |  | Distributors facility | N/V | ADS | BS 5419 | 200 | Copper | 95 | N/A |  | Copper | 70 | Yes | Copper | 25 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.08O | Y | Estates Stores | 2020-09-03 | TN-S | 3 Phase 4 wire | AC | 4.12 | 0.1 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 250 | Copper | 50 | N/A |  | Copper | 25 | Yes | Copper | 25 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
3.037 | Y | Felden Hall | 2020-09-03 | TN-S | 3 Phase 4 wire | AC | 3.2 | 0.06 | BS 88 - 2 type Gg | 200 | 80 | Distributors facility | 160 | ADS | BS EN 60947 - 2 MCCB | 200 | Copper | 95 | N/A |  | Copper | 50 | Yes | Copper | 25 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
1.132 | N | Forth House, 107 Kirby Corner Road | 2020-09-03 | [10 empty] | ADS
3.014 | Y | Furniture Store / Drama Store (Westwood) | 2020-09-03 | TN-S | 3 Phase 4 wire | AC | 2.38 | 0.12 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 250 | Copper | 25 | N/A |  | Copper | 25 | Yes | Copper | 25 | Yes | N/A | Yes | N/A | N/A | Yes | N/A
3.055 | N | Felden Garages | 2020-09-03 | [10 empty] | ADS
3.019 | Y | Garages,and Vehicle Workshop (W.W.) | 2020-09-08 | TN-S | 3 Phase 4 wire | AC | 0.31 | 0.73 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 2.5 | N/A |  | Copper | MICC | Lim | Copper | LIM | Lim | N/A | Lim | N/A | N/A | Lim | N/A
3.018 | Y | Garage and Exam Stores (Westwood) | 2020-09-08 | TN-S | 3 Phase 4 wire | AC | 0.43 | 0.53 | N/A | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 4 | N/A |  | Copper | MICC | Yes | Copper | N/A | Lim | N/A | Lim | N/A | N/A | Lim | N/A
1.067 | N | Gas Govenor Cryfield Ho.(off Gibbet hill) | 2020-09-08 | [10 empty] | ADS
1.24O | N | Gas Govenor Ho. (Adj Boiler House) | 2020-09-08 | [10 empty] | ADS
3.029 | N | Gas Govenor Ho Westwood Charter Avenue | 2020-09-08 | [10 empty] | ADS
3.03 | N | Gas Govenor Ho. Wrestwood Cedar Car Park | 2020-09-08 | [10 empty] | ADS
1.011 | Y | Gatehouse (Security) | 2020-09-08 | TN-S | 3 Phase 4 wire | AC | 0.86 | 0.06 | BS EN 60947 - 2 MCCB | 100 | 16 | Distributors facility | 100 | ADS | BS EN 60947 - 2 MCCB | 250 | Copper | 95 | N/A |  | Copper | 50 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
2.022 | N | Gibbet Hill Energy Centre | 2020-09-11 | [10 empty] | ADS
2.004 | Y | Gibbet Hill Academic Building( Bio Science) | 2020-09-11 | TN-S | 3 Phase 4 wire | AC | 9.82 | 0.05 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 1600 | Copper | 500 | N/A |  | Steel | Armour | Lim | Copper | 50 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
2.003 | Y | Gibbet Hill Farmhouse | 2020-09-11 | TN-S | 3 Phase 4 wire | AC | 4.8 | 0.1 | LIM | LIM |  | Distributors facility | N/V | ADS | BS 5419 | 200 | Copper | 95 | N/A |  | Copper | 50 | Yes | Copper | 25 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.408 | N | Arts Centre Goose Nest | 2020-09-11 | [10 empty] | ADS
3.027 | Y | Gosford | 2020-09-11 | TN-S | 3 Phase 4 wire | AC | 3.86 | 0.11 | LIM | LIM |  | Distributors facility | N/V | ADS | BS 5419 | 160 | Copper |  | N/A |  | Copper | N/A | N/A | Copper | N/A | Lim | Yes | Yes | N/A | N/A | N/A | N/A
3.057 | N | Gosford Plant Room | 2020-09-14 | [10 empty] | ADS
3.02O | Y | Graduate Studies and Educational studies | 2020-09-14 | TN-S | 3 Phase 4 wire | AC | 2.52 | 0.18 | LIM | LIM |  | Distributors facility | N/V | ADS | BS 5419 | 160 | Aluminium | 70 | N/A |  | Steel | Armour | Lim | Copper | 25 | Lim | Yes | Yes | N/A | N/A | N/A | N/A
3.052 | Y | Groundsman Store (adj tennis court) | 2020-09-14 | TN-S | 1 Phase 2 Wire | AC | 0.19 | 1.21 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | 100 | Copper | 4 | N/A |  | Copper | 4 | Yes | Copper | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
3.026 | Y | Hampton | 2020-09-14 | TN-S | 3 Phase 4 wire | AC | 0.12 | 3.6 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 3 | LIM | Copper | 120 | N/A |  | Steel | Armour | Lim | Copper | 25 | Lim | Yes | Yes | N/A | N/A | N/A | N/A
3.056 | N | Hampton Plant Room | 2020-09-14 | [10 empty] | ADS
1.01O | Y | Health Centre | 2020-09-14 | TN-S | 3 Phase 4 wire | AC | 1.76 | 0.26 | LIM | LIM |  | Distributors facility | N/V | ADS | BS 5419 | 100 | Aluminium | 25 | N/A |  | Steel | Armour | Lim | Copper | 16 | Lim | Yes | Yes | Yes | N/A | N/A | N/A
1.174 | Y | Heronbank Residences North and East Court | 2020-09-14 | TN-C-S | 3 Phase 4 wire | AC | 2.7 | 0.17 | LIM | LIM |  | Distributors facility | N/V | ADS | BS EN 60947 - 2 ACB | 1250 | Copper | 400 | N/A |  | Steel | Armour | Yes | Copper | 150 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.176 |  | Heronbank Residences West Court | 23/09/15 | TN-S | 3 Phase 4 wire | AC | 4.6 | 0.1 | LIM | LIM |  | Distributors facility | n/v | ADS | BS EN 60947 - 2 MCCB | 1250 | Copper | 150 | N/A |  | Copper | Armour | Yes | Copper | 150 | Yes | Yes | Yes | Lim | N/A | N/A | N/A
1.176 |  | Heron Bank West Laundry | 23/09/2015 | TN-S | 3 Phase 4 wire | AC | 4.6 | 0.1 | LIM | LIM |  | Distributors facility | n/v | ADS | BS EN 60947 - 2 MCCB | 1250 | Copper | 150 | N/A |  | Copper | Armour | Yes | Copper | 150 | Yes | Yes | Yes | Lim | N/A | N/A | N/A
1.131 |  | Heronbank Staff Flats | 15/03/2021 | TN-S | 3 Phase 4 wire | AC | LIM | LIM | LIM | LIM |  | Distributors facility | n/v | ADS | BS EN 60947 - 2 MCCB | 1250 | Copper | LIM | N/A |  | Copper | 70 | Yes | Copper | 35 | Yes | Yes | Yes | Lim | Lim | Lim | N/A
1.079 |  | Heronbank Gardeners Store | 2014-12-06 | TN-S | 3 Phase 4 wire | AC | 2.84 | 0.15 | LIM | LIM |  | Distributors facility | n/v | ADS | BS EN 60947 - 3 | 125 | Copper | 35 | N/A |  | Steel | Armour | Lim | Copper | 10 | Yes | Yes | N/A | N/A | N/A | N/A | N/A
1.047 |  | Humanities Building | 2015-02-02 | TN-S | 3 Phase 4 wire | AC | 2.68 | 0.17 | LIM | LIM |  | Distributors facility | n/v | ADS | BS EN 60947 - 3 | 1600 | Copper | 400 | N/A |  | Copper | 185 | Yes | Copper | 95 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.048 |  | Humanities Extension (Psychology) | 13/01/2015 | TN-S | 3 Phase 4 wire | AC | 3,02 | 0.15 | LIM | LIM |  | Distributors facility | n/v | ADS | BS 5419 | 300 | Copper | 185 | N/A |  | Copper | 50 | N/A | Copper | 50 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.047 |  | Humanities Café | 2020-10-08 | TN-S | 3 Phase 4 wire | AC | 2.68 | 0.17 | LIM | LIM |  | Distributors facility | n/v | ADS | BS EN 60947 - 3 | 1600 | Copper | 400 | N/A |  | Copper | 185 | Yes | Copper | 95 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.258 |  | Institute House (Institute of Ops. Man.) | 25/01/2020 | TN-C-S | 3 Phase 4 wire | AC | 3.2 | 0.15 | BS1361 - Type 1 | 80 |  | Distributors facility | n/v | ADS | BS EN 60947 - 3 | 250 | Copper | 25 | N/A |  | Copper | 35 | Yes | Copper | 10 | yes | Yes | Yes | Yes | N/A | Yes | Yes
1.016 |  | International House | 15/05/2014 | TN-C-S | 3 Phase 4 wire | AC | 3.2 | 0.15 | BS1361 - Type 1 | 80 |  | Distributors facility | n/v | ADS | BS EN 60947 - 3 | 250 | Copper | 25 | N/A |  | Copper | 35 | Yes | Copper | 10 | Yes | Yes | Yes | Yes | N/A | Yes | Yes
1.016 |  | International House Laundry | 20/04/2021 | TN-S | 3 Phase 4 wire | AC | 2.69 | n/a | LIM | LIM |  | Distributors facility | n/v | ADS | BS EN 60947 - 3 | 250 | Copper | 25 | N/A |  | Copper | 25 | Yes | Copper | 25 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
1.054 |  | International Manufacturing Cent. (Ph. 1 - 4) | 2015-05-10 | TN-S | 3 Phase 4 wire | AC | 4.8 | 0.1 | BS EN 60947 - 2 ACB | 200 |  | Distributors facility | n/v | ADS | BS EN 60947 - 2 ACB | 2000 | Copper | 10 | N/A |  | Copper | 630 | Yes | Copper | 50 | Yes | Yes | Yes | N/A | N/A | Yes | N/A
1.055 |  | I.M.C. Storage shed | [11 empty] | ADS | [6 empty] | Copper | 90 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.379 |  | I.M.C. Chiller Compound | [11 empty] | ADS
1.364 |  | I.I.N.M.-Int. Inst. Nanocomposite Man. Centre | 14/07/2020 | TN-S | 3 Phase 4 wire | AC | 2.82 | 0.19 | BS EN 60947 - 2 MCCB | 640 |  | Distributors facility | n/v | ADS | BS EN 60947 - 2 MCCB | 600 | Copper | 2x18 | N/A |  | Copper | 90 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.309 |  | I.I.P.S.I. | 24/06/2020 | TN-S | 3 Phase 4 wire | AC | 9.42 | 0.05 | LIM | LIM | LIM | Distributors facility | n/v | ADS | BS EN 60947 - 2 MCCB | 400 | Copper | 2x | N/A |  | Copper | 150 | Yes | Copper | 25 | Yes | Yes | Yes | Yes | N/A | Yes | Yes
2.036 |  | I.B.R.B.- Interdisciplinary Biomedical Research | [11 empty] | ADS
1.006 |  | I.A.R.C. International Automotive Research C. | 2020-10-06 | TN-S | 1 phase 3 wire | AC | 6.2 | 0.08 | LIM | LIM | LIM | Distributors facility | n/v | ADS | BS EN 60947 - 2 ACB | 3200 | Copper | 3x30 | N/A |  | Copper | 150 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.128 |  | Irvingdale 115 Kirby Corner Road | TO BE | DEMOLISHED
1.213 |  | Jack Martin Residences - 1 | 19/07/2018 | TN-S | 3 Phase 4 wire | AC | 6.96 | 0.07 | LIM | n/a | n/a | Distributors facility | n/v | ADS | BS EN 60947 - 2 ACB | 1600 | Copper | 8x400. | N/A |  | Copper | 400 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
1.214 |  | Jack Martin Residences - 2 | 2012-09-07 | TN-S | 3 Phase 4 wire | AC | 5.9 | 0.07 | LIM | LIM | n/a | Distributors facility | n/v | ADS | BS EN 60947 - 3 | 250 | Copper | 300 | N/A |  | Copper | 95 | Yes | Copper | 50 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.215 |  | Jack Martin Residences - 3 | 2017-07-07 | TN-S | 3 Phase 4 wire | AC | 3.86 | 0.12 | N/A | N/A | N/A | Distributors facility | n/v | ADS | BS EN 60947 - 3 | 250 | Copper | 185 | N/A |  | Copper | 50 | Yes | Copper | 50 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.216 |  | Jack Martin Residences - 4 | 19/07/2012 | TN-S | 3 Phase 4 wire | AC | 3.96 | 0.12 | N/A | N/A | N/A | Distributors facility | n/v | ADS | BS EN 60947 - 3 | 250 | Copper | 300 | N/A |  | Aluminium | SWA | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
|  | Jack Martin Laundry | [11 empty] | ADS
3.028 |  | Knightcote | 2016-01-07 | TN-S | 3 Phase 4 wire | AC | 3.28 | 0.14 | N/A | N/A | N/A | Distributors facility | n/v | ADS | BS 5419 | 160 | Copper | 120 | N/A |  | Copper | 50 | Yes | Copper | 25 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
3.028 |  | Knightcote Laundry | [11 empty] | ADS
3.058 |  | Knightcote Plant Room | 15/09/2020 | TN-S | 3 Phase 4 wire | AC | 3.28 | 0.14 | N/A | N/A | N/A | Distributors facility | N/A | ADS | BS 5419 | 160 | Copper | 120 | N/A |  | Copper | 50 | Yes | Copper | 25 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.13O |  | Lakemba, 111 Kirby Corner Road | 17/09/2019 | TN-C-S | 1 Phase 2 Wire | AC | 1.1 | 0.21 | BS1361 - Type 2 | 100 | 33 | Distributors facility | N/A | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | N/A | N/A | N/A | N/A | N/A
1.149 |  | Lakeside Residences-1 | 19/03/2014 | TN-S | 3 Phase 4 wire | AC | 6.1 | 0.06 | BS 88 - 2 type Gg | 250 | 80 | Distributors facility | N/A | ADS | BS 5419 | 800 | Copper | 300 | N/A |  | Copper | 150 | Yes | Copper | 35 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
1.149 |  | Lakeside 1 Laundry | [11 empty] | ADS
1.15O |  | Lakeside Residences-2 | 2021-10-03 | TN-S | 3 Phase 4 wire | AC | lim | lim | LIM | lim | lim | Distributors facility | n/a | ADS | BS 5419 | 800 | Copper | 300 | n/a |  | Copper | 150 | Yes | Copper | 35 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.151 |  | Lakeside Residences-3 | 16/03/2021 | TN-S | 3 Phase 4 wire | AC | 7.2 | 0.07 | LIM | lim | lim | Distributors facility | n/a | ADS | BS 5419 | 800 | Copper | 2x40 | N/A |  | Copper | 150 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
1.152 |  | Lakeside Residences-4 | 17/03/2021 | TN-C-S | 3 Phase 4 wire | AC | 7.2 | 0.07 | LIM | lim | lim | Distributors facility | n/a | ADS | BS 5419 | 800 | Copper | 2x40 | N/A |  | Copper | 2x95 | Yes | Copper | 50 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.152 |  | Lakeside 4 Laundry | [11 empty] | ADS |  |  |  |  | N/A
1.135 |  | Lakeside Staff Flats | 18/05/2021 | TN-S | 3 Phase 4 wire | AC | lim | lim | LIM | LIM | LIM | Distributors facility | n/a | ADS | BS 5419 | 400 | Copper | 2x | N/A |  | Copper | 95 | Yes | Copper | 35 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
1.368 |  | Lakeside Storage Shed (adj. Tennis Courts) | [11 empty] | ADS
1.256 |  | Lakeside Storage Shed (adj.Sherbourne ) | 30/06/2017 | TN-S | 1 Phase 2 Wire | AC | 0.65 | 0.35 | N/A | N/A | N/A | Distributors facility | n/a | ADS | BS 5419 | 100 | Copper | 25 | n/a |  | Copper | 16 | Yes | n/a | n/a | Lim | N/A | N/A | N/A | N/A | N/A | N/A
15.001 |  | Leamington Town Hall Learning Grid | [11 empty] | ADS
1.045 |  | Library | 29/06/2020 | TN-S | 3 Phase 4 wire | AC | lim | lim | DNO | DNO | DNO | Distributors facility | DNO | ADS | BS 5419 | 400 | Copper | 2x185 | N/A |  | Copper | 2x255 | Yes | Copper | 35 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
|  | Library Ground Floor Café -2 | [11 empty] | ADS
|  | Library Kitchen + Restaurant - 1 | [11 empty] | ADS
|  | Library Coffee Shop 1st Floor - 3 | [11 empty] | ADS
1.046 |  | Library Extension | 29/06/2020 | TN-S | 3 Phase 4 wire | AC | lim | lim | DNO | DNO | DNO | Distributors facility | DNO | ADS | BS 5419 | 400 | Copper | 2x185 | N/A |  | Copper | 2x185 | Yes | Copper | 35 | Lim | Yes | Yes | Yes | N/A | N/A | N/A
3.025 |  | Loxley | 2020-07-09 | TN-S | 3 Phase 4 wire | AC | 3.2 | 0.1 | LIM | LIM | LIM | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | LIM | Copper | 95 | N/A |  | Copper | SWA | Lim | Copper | 25 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
3.025 |  | Loxley Laundry | 2020-07-09 | TN-S | 3 Phase 4 wire | AC | 3.2 | 0.1 | LIM | LIM | LIM | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | LIM | Copper | 95 | N/A |  | Copper | SWA | Lim | Copper | 25 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
|  | Loxley Plant Room | [11 empty] | ADS |  |  |  |  | N/A
1.284 |  | Materials + Analytic Science (adj.Physics) | 15/12/1017 | TN-S | 3 Phase 4 wire | AC | 11.88 | 0.03 | LIM | LIM | LIM | Distributors facility | n/a | ADS | BS EN 60947 - 2 ACB | 1600 | Copper | 2x800 | n/a |  | Copper | 240 | Lim | Copper | 50 | Lim | Yes | Yes | Yes | N/A | N/A | N/A
1.381 |  | Materials Engineering Centre | [11 empty] | ADS
1.133 |  | Marina, 105 Kirby Corner Road | 16/09/2019 | TN-C-S | 1 Phase 2 Wire | AC | 0.67 | 0.34 | BS1361 - Type 2 | 100 | 33 | Distributors facility | n/a | ADS | BS EN 60947 - 3 | LIM | Copper | lim | n/a |  | Copper | lim | lim | Copper | lim | lim | Lim | Lim | N/A | N/A | lim | N/A
2.011 |  | Maths Research House 1 | 2022-06-15 | TN-C-S | 1 Phase 2 Wire | AC | 0.44 | 0.53 | BS1361 - Type 2 | 60 | 33 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 100 | Copper | 25 | n/a |  | Copper | 10 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
2.012 |  | Maths Research House 2 | 2022-06-15 | TN-C-S | 1 Phase 2 Wire | AC | 0.39 | 0.59 | BS1361 - Type 2 | 60 | 33 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 100 | Copper | 25 | n/a |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
2.013 |  | Maths Research House 3 | 2022-06-15 | TN-C-S | 1 Phase 2 Wire | AC | 0.56 | 0.27 | BS1361 - Type 2 | 60 | 33 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
2.014 |  | Maths Research House 4 | 2022-06-15 | TN-C-S | 1 Phase 2 Wire | AC | 0.5 | 0.46 | BS1361 - Type 2 | 60 | 33 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
2.015 |  | Maths Research House 5 | 2022-06-15 | TN-C-S | 1 Phase 2 Wire | AC | 0.85 | 27 | BS1361 - Type 2 | 60 | 33 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 100 | Copper | 25 | 30mA | 17.9 | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
2.016 |  | Maths Research House 6 | 2022-06-15 | TN-C-S | 1 Phase 2 Wire | AC | 0.66 | 0.35 | BS1361 - Type 2 | 60 | 33 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
2.027 |  | Mechanochemical Cell Biology | 2022-06-15 | TN-S | 3 Phase 4 wire | AC | 8.22 | 0.06 | BS 88 - 2 type Gg |  | 80 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB |  | Copper | 300 | N/A |  | Copper | 95 | Yes | Copper | 25 | Yes | N/A | N/A | Yes | N/A | Yes | N/A
|  | Mechanochemical Cell Biology Extension | [11 empty] | ADS
2.008 |  | Medical School Teaching Building | 2022-06-15 | TN-S | 3 Phase 4 wire | AC | lim | lim | LIM |  |  | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 400 | Copper | 240 | N/A |  | Copper | 120 | Yes | Copper | 35 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.005 |  | Milburn House | 2022-06-15 | TN-S | 3 Phase 4 wire | AC | lim | lim | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 1000 | Copper | 500 | N/A |  | Copper | 300 | Yes | Copper | 95 | Yes | Yes | Yes | Yes | N/A | Yes | Yes
2.007 |  | MRC Laboratory | 2022-06-15 | TN-S | 3 Phase 4 wire | AC | 1.58 | 0.12 | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 250 | Copper | 120 | N/A |  | Copper | 95 | Yes | Copper | 50 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
3.007 |  | Music Centre | 2022-06-15 | TN-C-S | 3 Phase 4 wire | AC | lim | lim | lim | lim | lim | Distributors facility | lim | ADS | lim | lim | Copper | 10 | N/A |  | Copper | 10 | Yes | Copper | 16 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
1.175 |  | N.A.I.C. | [11 empty] | ADS
3.004 |  | New Education (CEDAR) | 2022-06-15 | TN-S | 3 Phase 4 wire | AC | 2.4 | 0.29 | lim | lim | lim | Distributors facility | lim | ADS | BS 5419 | 225 | Copper | 50 | N/A |  | Steel | 120 | Yes | Copper | 16 | Yes | Yes | Yes | Yes | N/V | N/A | N/A
1.255 |  | Nursery Lakeside | 2022-06-15 | TN-S | 3 Phase 4 wire | AC | lim | lim | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 1000 | Copper | 500 | N/A |  | Copper | 35 | Yes | Copper | 10 | Yes | Yes | N/A | Yes | N/A | N/A | N/A
1.007 |  | Physical Sciences | 2022-06-15 | TN-S | 3 Phase 4 wire | AC | lim | lim | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 250 | Copper | 95 | N/A |  | Copper | 50 | Yes | Copper | 25 | Yes | Yes | N/A | N/A | N/A | Yes | N/A
1.323 |  | Phytobiology Facility | 2022-06-15 | TN-S | 3 Phase 4 wire | AC | 0.96 | 0.05 | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | lim | Copper | 240 | N/A |  | Copper | 50 | Yes | Copper | 25 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
1.324 |  | Phytobiology Plant Container | 2022-06-15 | TN-S | 3 Phase 4 wire | AC | 1.01 | 0.05 | BS EN 60947 - 2 MCCB | 200 | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 250 | Copper | 95 | N/A |  | Steel | 120 | Yes | Copper | 10 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
1.042 |  | Physics | 2022-06-15 | TN-C-S | 3 Phase 4 wire | AC | lim | lim | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 1000 | Copper | lim | N/A |  | Copper | 185 | Yes | Copper | lim | lim | lim | lim | lim | lim | lim | lim
1.043 |  | Physics External Store | 2022-06-15 | TN-S | 3 Phase 4 wire | AC | 8.9 | 0.08 | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 1000 | Copper | lim | N/A |  | Copper | 185 | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
3.013 |  | Post Room | 2022-06-15 | TN-S | 3 Phase 4 wire | AC | 0.86 | 0.52 | BS 88 - 2 type Gg | 63 | 80 | Distributors facility | lim | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
3.003 |  | Print Services | 2022-06-15 | TN-S | 3 Phase 4 wire | AC | 3.62 | 0.13 | BS 88 - 2 type Gg | 150 | 80 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 200 | Copper | 50 | N/A |  | Copper | 25 | Yes | Copper | 16 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.004 |  | Radcliffe House | [11 empty] | ADS
|  | Radcliffe House Bar , Restaurant and Kitchen | 2022-06-15 | TN-S | 3 Phase 4 wire | AC | lim | lim | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 1000 | Copper | 185 | N/A |  | Copper | 25 | lim | Copper | 50 | lim | Yes | Yes | Yes | N/A | YES | N/A
1.018 |  | Ramphal Building | 2022-06-15 | TN-S | 3 Phase 4 wire | AC | 4.62 | 0.1 | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 3 | 1000 | Copper | 500 | N/A |  | Copper | 95 | Yes | Copper | 50 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
|  | Ramphal Kitchen and Restaurant | [11 empty] | ADS
|  | Redfern Laundry | [11 empty] | ADS
1.2OO |  | Rootes Residences (A - C) | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | 3.18 | 0.16 | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 400 | Copper | 120 | N/A |  | Copper | 95 | Yes | Copper | 25 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.201 |  | Rootes Residences (D - H) | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | 4.02 | 0.12 | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 500 | Copper | 120 | N/A |  | Copper | 95 | Yes | Copper | 25 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.202 |  | Rootes Residences (J - L) | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | 4.07 | 0.06 | lim | lim | lim | Distributors facility | lim | ADS |  | N/A | Copper | 240 | N/A |  | Copper | 400 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
1.203 |  | Rootes Residences (M - P) | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | 7.2 | 0.06 | lim | lim | lim | Distributors facility | lim | ADS |  | N/A | Copper | 240 | N/A |  | Copper | 240 | Yes | Copper | 50 | Yes | Yes | N/A | Yes | N/A | N/A | N/A
1.013 |  | Rootes Social Building | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | 15.8 | 0.03 | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | LIM | Copper | 150 | N/A |  | Copper | 185 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
|  | Rootes Social Building Second Floor Kitchen | [11 empty] | ADS | [14 empty] | N/V
|  | Rootes Social Building Ground Floor Kitchen | [11 empty] | ADS
|  | Rootes Social 1st Floor Fusion Kitchen | [11 empty] | ADS
|  | Rootes 1st Floor Restaurant | [11 empty] | ADS
|  | Rootes Social 1st Floor Bar | [11 empty] | ADS
|  | Rootes Social Panama Bar | [11 empty] | ADS
|  | Rootes Soc. Costa | [11 empty] | ADS
1.015 |  | Rootes/Students Union Laundry | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | lim | lim | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.015 |  | Rootes Staff Housing Wardens Ho. flat 5 | 2022-06-22 | TN-S | 1 Phase 2 Wire | AC | lim | lim | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 3 | 100 | Copper | 16 | N/A |  | Copper | 10 | Yes | Copper | 10 | Yes | N/A | N/A | N/A | N/A | N/A | N/A
2.026 |  | Satellite Exchange | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | 0.08 | 0.56 | BS 88 - 2 type Gg | 100 | 80 | Distributors facility | lim | ADS | BS EN 60947 - 3 | 125 | Copper | 50 | N/A |  | Aluminium |  | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1.002 |  | Scarman House | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | 46 | 0.01 | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 800 | Copper | 500 | N/A |  | Copper | 300 | Yes | Copper | 35 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
|  | Scarman House Bar and Restuarants | [11 empty] | ADS
|  | Scarman House Kitchen | [11 empty] | ADS
1.259 |  | Schmitt Building | 2022-06-22 | TN-C-S | 3 Phase 4 wire | AC | 2.58 | 0.18 | BS1361 - Type 2 | 100 | 33 | Distributors facility | lim | ADS | BS EN 60947 - 3 | 125 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 16 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.027 |  | Science Block A | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | 19.9 | 0.01 | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 1000 | Copper |  | N/A |  | Copper | 95 | Yes | Copper | 25 | N/V | N/V | N/V | N/V | N/V | N/V | N/V
1.028 |  | Science Block B | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | lim | lim | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 3 | 1000 | Copper | 630 | N/A |  | Copper | 120 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.029 |  | Science Block C | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | lim | lim | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 3 | 1000 | Copper | 630 | N/A |  | Copper | 120 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.03O |  | Science Block D | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | 15.3 | 0.02 | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 1000 | Copper |  | N/A |  | Copper | 95 | Yes | Copper | 25 | Yes | Yes | Yes | N/A | N/A | Yes | N/A
1.031 |  | Science Block E | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | lim | lim | lim | lim | lim | Distributors facility | lim | ADS
1.032 |  | Science Block F | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | lim | lim | lim | lim | lim | Distributors facility | lim | ADS
1.022 |  | Science Block G | 2022-06-22 | TN-S | 3 Phase 4 wire | AC | 4.4 | 0.06 | lim | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 3 | 200 | Copper | 120 | N/A |  | Copper | 50 | Yes | Copper | 25 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.319 |  | Science Gas Store - 1 (Storage Garages) | [11 empty] | ADS
1.32O |  | Science Gas Store - 2 (Storage Garages) | [11 empty] | ADS
1.321 |  | Science Gas Store - 3 (Storage Garages) | [11 empty] | ADS
1.322 |  | Science Gas Store - 4 (Storage Garages) | [11 empty] | ADS
1.033 |  | Science C Solvent Store | [11 empty] | ADS
1.035 |  | Science D - Wood Shed | 2022-10-12 | TN-C-S | 3 Phase 4 wire | AC | lim | lim | lim | lim | lim | Distributors facility | lim | ADS | lim | lim | lim | lim | N/A |  | Copper | 50 | Yes |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1.034 |  | Science D Fuel Store | 2022-10-12 | TN-S | 3 Phase 4 wire | AC | 9.4 | 0.07 | LIM | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 3 | 100 | Copper | lim | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1.277 |  | Science D Gases B | [11 empty] | ADS | [6 empty] | Copper
1.036 |  | Science D Underground Rotating Disk Test Cell | 2022-10-12 | TN-S | 3 Phase 4 wire | AC | 2.75 | 0.17 | LIM | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 400 | Copper | 150 | N/A |  | Steel | 230 | Yes | Copper | 25 | Yes | Yes | N/A | N/A | N/A | N/A | N/A
3.06O |  | Science Education Plant Room | 2022-10-12 | TN-S | 3 Phase 4 wire | AC | 2.02 | 0.23 | BS 88 - 2 type Gg | lim | 80 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 250 | Copper | 35 | N/A |  | Copper | 35 | Yes | Copper | 35 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.069 |  | Sewage Pumping Station | 2022-10-12 | TN-S | 3 Phase 4 wire | AC | 1.11 | 0.41 | LIM | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 100 | Copper | 50 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | N/A | N/A | N/A | N/A | N/A
1.31O |  | Sherbourne Residences Block - 1 | 2022-10-12 | TN-S | 3 Phase 4 wire | AC | 2.6 | 0.19 | BS EN 60947 - 3 | 250 | 25 | Distributors facility | lim | ADS | BS EN 60947 - 3 | 250 | Copper | 240 | N/A |  | Copper | 120 | Yes | Copper | 16 | Yes | Yes | N/A | N/A | N/A | N/A | N/A
1.31O |  | Sherborne 1 Laundry | 2022-10-12 | TN-S | 3 Phase 4 wire | AC | 2.6 | 0.19 | BS EN 60439 - 3 | 250 | 25 | Distributors facility | lim | ADS | BS EN 60439 - 3 | 250 | Copper | 240 | N/A |  | Copper | 120 | Yes | Copper | 16 | Yes | Yes | N/A | N/A | N/A | N/A | N/A
1.311 |  | Sherbourne Residences Block - 2 | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | 2.6 | 0.19 | BS EN 60947 - 3 | 250 | 36 | Distributors facility | 200 | ADS | BS EN 60439 - 3 | 250 | Copper | 240 | N/A |  | Copper | 120 | Yes | Copper | 16 | Yes | Yes | Yes | N/A | N/A | Yes | N/A
1.312 |  | Sherbourne Residences Block - 3 | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | 3.52 | 0.13 | LIM | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 250 | Copper | 185 | N/A |  | Copper | 120 | Yes | Copper | 16 | Yes | Yes | N/A | Yes | N/A | Yes | Yes
1.313 |  | Sherbourne Residences Block - 4 | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | 3.94 | 0.12 | LIM | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 250 | Copper | 185 | N/A |  | Copper | 120 | Yes | Copper | 16 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
1.314 |  | SherbournesResidences Block - 5 | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | 20.2 | 0.02 | LIM | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 3 | 250 | Copper | 150 | N/A |  | Copper | 120 | Yes | Copper | 16 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
1.314 |  | Sherborne 5 Laundry | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | 2.12 | 0.22 | LIM | lim | lim | Distributors facility | lim | ADS
1.315 |  | Sherbourne Residences Block - 6 | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | 2.4 | 0.21 | LIM | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 250 | Copper | 185 | N/A |  | Copper | 120 | Yes | Copper | 16 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
.1.370 |  | Sherbourne Residences Block - 7 | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | 15.9 | 0.01 | BS EN 60947 - 2 MCCB | 1250 | 35 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 125 | Copper | 185 | N/A |  | Steel | 255 | Yes | Copper | 25 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
1.371 |  | Sherbourne Residences Block - 8 | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | 15.9 | 0.01 | BS EN 60947 - 2 MCCB | 1250 | 35 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 125 | Copper | 185 | N/A |  | Steel | 255 | Yes | Copper | 25 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
1.372 |  | Sherbourne Residences Block - 9 | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | 15.9 | 0.01 | BS EN 60947 - 2 MCCB | 1250 | 35 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 125 | Copper | 185 | N/A |  | Steel | 255 | Yes | Copper | 25 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
1.316 |  | Sherbourne Energy Centre - 1 | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | [6 empty] | lim | ADS
1.383 |  | Sherbourne Energy Centre - 2 | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | [6 empty] | lim | ADS
1.384 |  | Sherbourne Accomodation Managers | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | 1.7 | 0.14 |  | 125 | 35 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 125 | Copper | 95 | N/A |  | Steel | 131 | Yes | Copper | 25 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
1.373 |  | The Slate Conferencies | [10 empty] | 1250 | ADS
1.041 |  | Social Sciences North and South Block - A | 2022-10-15 | TN-C-S | 3 Phase 4 wire | AC | 3.54 | 0.13 | LIM | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 400 | Copper | 240 | N/A |  | Copper | 120 | Yes | Copper | 95 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.039 |  | Social Sciences B and C | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | 1.6 | 0.28 | LIM | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 3 | 125 | Copper | 35 | N/A |  | Copper | 35 | Yes | Copper | Lim | Lim | Lim | Lim | Lim | Lim | Lim | Lim
1.04O |  | Social Sciences D and E | 2022-10-15 | TN-C-S | 3 Phase 4 wire | AC | 2.28 | 0.2 | LIM | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 400 | Copper | 240 | N/A |  | Copper | 95 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
|  | Social Sciences Café Kitchen | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | 5.36 | 0.1 | LIM | lim | lim | Distributors facility | lim | ADS | BS EN 60947 - 3 | 125 | Copper | 50 | N/A |  | Copper | 25 | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1.038 |  | Social Sciences FME | 2022-10-15 | TN-S | 3 Phase 4 wire | AC | 5.08 | 0.08 | LIM | lim | lim | Distributors facility | lim | ADS | BS 5419 | 100 | Aluminium |  | N/A |  | Steel | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V
1.376 |  | Sports Centre Complex | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | 4.44 | 0.04 | BS EN 60947 - 2 MCCB | 2500 | 50 | Distributors facility | 1745 | ADS | BS EN 60947 - 2 MCCB | 2500 | Copper | 3x630 | N/A |  | Copper | 300 | Yes | Copper | 50 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
1.057 |  | Sports Centre now Junction | 2022-10-17 | TN-C-S | 3 Phase 4 wire | AC | 10.6 | 0.04 | BS 88 - 2 type Gg | 315 | 80 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 315 | Copper | 2x95 | N/A |  | Copper | 95 | Yes | Copper | 50 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.376 |  | Sport Centre Swimming Pool (Wet Area)
1.159 |  | Sports Pavilion Cryfield | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | 3.06 | 0.15 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 600 | Copper | 2x240 | N/A |  | Copper | 2x120 | Yes | Copper | 25 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
1.023 |  | Staff Accomodation - Nightline | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 125 | Copper | 35 | N/A |  | Copper | 50 | Yes | Copper | 16 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.052 |  | Students Union North | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | 0.42 | 0.1 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 2000 | Copper | 3x400 | N/A |  | Copper | 95 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
Xananas Kitchen
Xananas Bar and Restaurant.
1.053 |  | Students Union South | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | 12 | 0.04 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 2000 | Copper | 2x185 | N/A |  | Copper | 185 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
|  | Dirty Duck Bar and Kitchen | [10 empty] | lim | ADS
|  | Copper Rooms Bars 1 and 2 | [10 empty] | lim | ADS
|  | Terrace Bar | [10 empty] | lim | ADS
|  | Rouge Bar | [10 empty] | lim | ADS
|  | Curiositea | [10 empty] | lim | ADS
|  | The Bread Oven | [10 empty] | lim | ADS
|  | Unit-2 (Formerly Bank ) | [10 empty] | lim | ADS
1.07O |  | Surface Water Pumping Station | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 25 | N/A |  | Copper | N/V | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1.071 |  | Substation No.1 (Primary at Boiler House) + M.P. | 2022-10-17 | DB ONLY | [8 empty] | lim | ADS
1.03O.LOO.027 |  | Substation No.2 ( Science Engineering ) +M.P. | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | 15.3 | 0.02 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 1600 | Copper | BAR | N/A |  | Copper | 95 | Yes | Copper | 25 | Yes
1.028.L00.014 |  | Substation No.3 ( Molecular Science ) +M.P. | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | 15.3 | 0.02 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 1600 | Copper | BAR | N/A |  | Copper | 120 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.028.LOO.017 |  | Substation No.4 (Physics ) + MAIN PANEL | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | 8.5 | 0.03 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 1600 | Copper | BAR | N/A |  | Copper | 185 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.072 |  | Substation No.5 (Sports Centre) + MAIN PANEL. | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | 16 | 0.06 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 1600 | Copper | 2X500 | N/A |  | Copper | 300 | Yes | Copper | 50 | Yes | N/A | N/A | Yes | N/A | Yes | N/A
1.073 |  | Substation No. 6 (Tocil Flats).+ MAIN PANEL | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | 19.9 | 0.01 | BS EN 60947 - 2 ACB | 1600 | 65 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 1600 | Copper | 300 | LIM |  | Steel | 2X50 | Yes | Copper | 300 | Yes | N/A | N/A | N/A | N/A | Yes | N/A
|  | Substation No.7 (Butterworth Students union) | [10 empty] | lim | ADS
1.246 |  | Substation No.8 (Jack Martin Halls)+M.P. | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | 6.96 | 0.07 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 1600 | Copper | 8x400 | N/A |  | Copper | 400 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
1.013 |  | Substation No.9 (Rootes Social)+M.P. | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | 9.37 | 0.04 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 200 | Copper | BAR | N/A |  | Copper | 185 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.001.L00.148 |  | Substation No.10 (Arts Centre Senate Soc. Study) | [10 empty] | lim | ADS
1.249 |  | Substation No.11 (Radcliffe House) | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | 9.8 | 0.04 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 1280 | Copper | 2X500 | N/A |  | Copper | 240 | Yes | Copper | 50 | Yes | N/V | N/V | Yes | N/A | Yes | N/A
1.074 |  | Substation No.12 (Cryfield Village)+M.P. | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 2000 | Copper | 2X300 | N/A |  | Copper | 185 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
2.006 LOO.054 |  | Substation No.13 (Bio Tech) | 2022-10-17 | TN-C-S | 3 Phase 4 wire | AC | 6.8 | 0.06 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 2500 | Copper | 500 | N/A |  | Copper | 185 | Yes | Copper | 95 | N/V | N/V | N/V | N/V | N/V | N/V | N/V
2.021 |  | Substation No.14 (Gibbet Hill)+M.P. | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | 9.82 | 0.05 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 1600 | Copper | 4x500 | N/A |  | Copper | 185 | Yes | Copper | 95 | Yes | Yes | Yes | N/A | N/A | Yes | N/A
3.049 |  | Substation No.15 (Westwood)+M.P. | 2022-10-17 | TN-S | 3 Phase 4 wire | AC | 8.12 | 0.06 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 1600 | Copper | 400 | N/A |  | Copper | 240 | Yes | Copper | 240 | N/V | N/V | N/V | N/V | N/V | N/V | N/V
1.006.LOO.037 |  | Substation No.16 (A.T.C.) + MAIN PANEL. | 2022-10-18 | TN-C-S | 3 Phase 4 wire | AC | 4.06 | 0.11 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 3200 | Copper | 3x300 | N/A |  | Copper | 150 | Yes | Copper | 50 | Yes | N/V | N/V | Yes | N/A | Yes | N/A
1.002 LOO.072 |  | Substation No.17 (Scarman) + MAIN PANEL. | 2022-10-18 | TN-C-S | 3 Phase 4 wire | AC | 33.7 | 0.01 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 1600 | Copper | 4x500 | N/A |  | Copper | 300 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.252 |  | Substation No.18 (Claycroft) + MAIN PANEL. | 2022-10-18 | TN-C-S | 3 Phase 4 wire | AC | 20 | 0.02 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 1600 | Copper | 4X120 | N/A |  | Copper | 95 | Yes | Copper | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V
1.075 |  | Substation No.19 (Int Man Cntr) +M.P. | 2022-10-18 | TN-S | 3 Phase 4 wire | AC | 4.8 | 0.1 | BS EN 60947 - 2 ACB | 2000 | 65 | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 2000 | Copper | N/V | N/A |  | Copper | 630 | Yes | Copper | 70 | Yes | Yes | Yes | N/A | N/A | Yes | N/A
1.076 |  | Substation No.20 (Lakeside) +M.P. | 2022-10-18 | TN-S | 3 Phase 4 wire | AC | 10.72 | 0.04 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 1250 | Copper | 500 | N/A |  | Copper | 300 | Yes | Copper | 25 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
01.066 L00.010 |  | Substation No.21 (C.H.P.) +M.P. | 2022-10-18 | TN-S | 3 Phase 4 wire | AC | 3.62 | 0.06 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | N/V | Copper | 2x300 | N/A |  | Copper | 95 | Yes | Copper | 2x35 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.064 |  | Sub Station No.22(Heronbank) + MAIN PANEL. | 2022-10-18 | TN-C-S | 3 Phase 4 wire | AC | 1.79 | 0.26 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 1250 | Copper | 630 | N/A |  | Copper | 300 | Yes | Copper | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V
1.065 |  | Substation No.23 (Maths and Stats)+ M. PANEL. | 2022-10-18 | TN-C-S | 3 Phase 4 wire | AC | 4 | 0.1 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 2500 | Copper | 630 | N/A |  | Copper | 300 | Yes | Copper | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V
1.078 |  | Substation No.24 (University House)+ MAIN P. | 2022-10-18 | TN-S | 3 Phase 4 wire | AC | 5.16 | 0.09 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | N/V | Copper | 150 | N/A |  | Copper | 70 | Yes | Copper | 35 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.297 |  | Substation No.25+25A (Milburn House)+M.P. | 2022-10-18 | TN-C-S | 3 Phase 4 wire | AC | 20.2 | 0.02 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | N/V | Copper | 630 | N/A |  | Copper | 300 | Yes | Copper | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V
T.B.C. |  | Substation No.26 (Digital Lab)+ MAIN PANEL. | 2022-10-18 | TN-S | 3 Phase 4 wire | AC | 4.15 | 0.1 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 1600 | Copper | 300 | N/A |  | Copper | 150 | Yes | Copper | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V
1.198 |  | Substation No.27 (Bluebell)+ MAIN PANEL. | 2022-10-18 | TN-C-S | 3 Phase 4 wire | AC | 9.98 | 0.04 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 1600 | Copper | 500 | N/A |  | Copper | 300 | Yes | Copper | 25 | N/V | N/V | N/V | N/V | N/V | N/V | N/V
T.B.C. |  | Substation No.28 (Argent Court)+ MAIN PANEL. | 2022-10-18 | TN-S | 3 Phase 4 wire | AC | 5.76 | 0.08 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | N/V | Copper | 240 | N/A |  | Copper | 120 | Yes | Copper | 25 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
T.B.C. |  | Substation No.29 (Sherbourne)+ MAIN PANEL. | 2022-10-18 | TN-C-S | 3 Phase 4 wire | AC | 6.65 | 0.06 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | N/V | Copper | 300 | N/A |  | Copper | 120 | Yes | Copper | 25 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
01.006 L01.018 |  | Substation No. 30 (Engine Test Facility)+M.P. | 2022-10-18 | TN-S | 3 Phase 4 wire | AC | 6.2 | 0.08 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 2500 | Copper | 3x300 | N/A |  | Copper | 150 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.199 |  | Substation No. 31 (I.I.N.M.)+ MAIN PANEL. | 2022-10-18 | TN-S | 3 Phase 4 wire | AC | 7.96 | 0.05 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 630 | Copper | 2x180 | N/A |  | Copper | 95 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
T.B.C. |  | Substation No.32 (Cryfield Energy Centre)+M.P. | 2022-10-18 | TN-S | 3 Phase 4 wire | AC | 13.3 | 0.03 | N/V | N/V | N/V | Distributors facility | lim | ADS | N/V | N/V | Copper | 630 | N/A |  | Copper | N/V | Yes | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V
T.B.C. |  | Substation No. 33(W.B.S.)+ MAIN PANEL. | 2022-10-18 | TN-C-S | 3 Phase 4 wire | AC | 4.98 | 0.08 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 2500 | Copper | 500 | N/A |  | Copper | 300 | Yes | Copper | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V
T.B.C. |  | Substation No. 34 (W.M.G.-I.M.M.C.-)+M.P. | 2022-10-18 | TN-S | 3 Phase 4 wire | AC | 9.2 | 0.04 | BS EN 60947 - 2 MCCB | 1250 | 1250 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 1250 | Copper | 2x400 | N/A |  | Copper | 300 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
T.B.C. |  | Substation No.35 (Oculus) +M.P. | 2022-10-18 | TN-C-S | 3 Phase 4 wire | AC | 11.3 | 0.04 | BS EN 60947 - 2 MCCB | 800 | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 800 | Copper | 500 | N/A |  | Copper | 185 | Yes | Copper | 50 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
T.B.C. |  | Substation No 36 (The Slate) +M.P. | 2022-10-18 | TN-C-S | 3 Phase 4 wire | AC | 8.2 | 0.05 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 1250 | Copper | 240 | N/A |  | Copper | 120 | Yes | Copper | 50 | Yes | Yes | N/A | N/A | N/A | Yes | N/A
T.B.C. |  | Substation No. 37 (Sherbourne) +M.P. | 2022-10-18 | TN-S | 3 Phase 4 wire | AC | 15.9 | 0.01 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 2x400 | Copper | 2x400 | N/A |  | Copper | 240 | Yes | Copper | 25 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
T.B.C. |  | Substation No. 38 | 2022-10-18 | TN-C-S | 3 Phase 4 wire | AC | 2.36 | 0.19 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 2500 | Copper | 630 | N/A |  | Copper | 300 | Yes | Copper | 95 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
T.B.C. |  | Substation No. 39 (W.M.G. Clean Room-I.A.R.C.) | 2022-10-18 | TN-C-S | 3 Phase 4 wire | AC | 8 | 0.05 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 3200 | Copper | N/V | N/A |  | Copper | 240 | Yes | Copper | 35 | Yes | Yes | N/V | Yes | N/A | Yes | N/A
T.B.C. |  | Substation No. 40 (Sports Pavillion) +M.P. | 2022-10-18 | TN-S | 3 Phase 4 wire | AC | 3.06 | 0.15 | BS EN 60947 - 2 MCCB | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 630 | Copper | 2x240 | N/A |  | Copper | 120 | Yes | Copper | 25 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
T.B.C. |  | Substation No.41 (M.E.H.) +M.P. | 2022-10-18 | TN-C-S | 3 Phase 4 wire | AC | 6.3 | 0.07 | BS EN 60947 - 2 MCCB | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | N/V | Copper | 500 | N/A |  | Copper | 300 | Yes | Copper | 50 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
T.B.C. |  | Substation No. 42 (B.R.B.) +M.P. | 2022-10-18 | DB ONLY | [8 empty] | lim | ADS
T.B.C. |  | Substation No. 43 (C.P.16 UNI House )+M.P. | [10 empty] | lim | ADS
T.B.C. |  | Substation No. 44 (Faculty of Arts) +M.P. | [10 empty] | lim | ADS
T.B.C. |  | Substation No. 51 (N.A.I.C.) +M.P. | [10 empty] | lim | ADS
1.129 |  | Sunnybrow, 113 Kirby Corner Road | TO BE | DEMOLISHED | [8 empty] | lim | ADS
1.134 |  | Tarl Lea, 103 Kirby Corner Road | 2022-10-24 | TN-C-S | 1 Phase 2 Wire | AC | 0.76 | 0.3 | BS1361 - Type 2 | 100 | 33 | Distributors facility | lim | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
3.059 |  | Tennis Centre ( Westwood ) | 2022-10-24 | TN-S | 3 Phase 4 wire | AC | 2.85 | 0.14 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 160 | Copper | 95 | N/A |  | Copper | 50 | Yes | Copper | 25 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.328 |  | Tennis Courts (Sherbourne ) | 2022-10-24 | [9 empty] | lim | ADS
1.366 |  | The Oculus Teaching and Learning Building | 2022-10-24 | TN-S | 3 Phase 4 wire | AC | 11 | 0.04 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 800 | Copper | 500 | N/A |  | Copper | 185 | Yes | Copper | 50 | Yes | Yes | N/A | Yes | N/A | Yes | N/A
7.001 |  | Titan | 2022-10-24 | TN-C-S | 3 Phase 4 wire | AC | 2.38 | 0.21 | BS1361 - Type 2 | 100 | 33 | Distributors facility | lim | ADS | BS EN 60947 - 3 | 125 | Copper | 16 | N/A |  | Copper | 25 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.204 |  | Tocil Block - 1 ( Flats 1 - 6 ) | 2022-10-24 | TN-S | 3 Phase 4 wire | AC | 4.14 | 0.1 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 300 | Copper | 150 | N/A |  | Copper | 95 | Yes | Copper | 25 | Yes | Yes | N/A | N/A | N/A | N/A | Yes
1.205 |  | Tocil Block - 2 ( Flats 7 - 12 ) | 2022-10-24 | TN-S | 3 Phase 4 wire | AC | 5 | 0.09 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 300 | Copper | 240 | N/A |  | Steel | 289 | Yes | Copper | 50 | Yes | Yes | N/A | N/A | N/A | N/A | Yes
1.206 |  | Tocil Block - 3 ( Flats 13 - 18 ) | 2022-10-24 | TN-S | 3 Phase 4 wire | AC | 4.4 | 0.1 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 300 | Copper | 240 | N/A |  | Steel | 289 | Yes | Copper | 50 | Yes | Yes | N/A | N/A | N/A | N/A | Yes
1.207 |  | Tocil Block - 4 ( Flats 19-24 ) | 2022-10-24 | TN-S | 3 Phase 4 wire | AC | 1.44 | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 200 | Copper | 240 | N/A |  | Copper | 40 | Yes | Copper | 25 | Yes | Yes | N/A | Yes | N/A | N/A | N/A
1.208 |  | Tocil Block - 5 ( Flats 25-30 ) | 2022-10-24 | TN-C-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 200 | Copper | 185 | N/A |  | Copper | 50 | Yes | Copper | 35 | Yes | Yes | Yes | N/A | N/A | N/A | Yes
1.209 |  | Tocil Block - 6 ( Flats 31-36 ) | 2022-10-24 | TN-C-S | 3 Phase 4 wire | AC | 4.8 | 0.09 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 300 | Copper | 240 | N/A |  | Copper | 50 | Yes | Copper | 25 | Yes | Yes | N/A | N/A | N/A | N/A | Yes
1.237 |  | Tocil Block - 7 ( Flats 37-42 ) | 2022-10-24 | TN-C-S | 3 Phase 4 wire | AC | 9.1 | 0.05 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 300 | Copper | 240 | N/A |  | Copper | 50 | Yes | Copper | 25 | Yes | Yes | N/A | N/A | N/A | N/A | Yes
1.21O |  | Tocil Block - 8 ( Flats 43-48 ) | 2022-10-24 | TN-C-S | 3 Phase 4 wire | AC | 7.92 | 0.04 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 300 | Copper | 240 | N/A |  | Copper | 240 | Yes | Copper | 50 | Yes | Yes | N/A | N/A | N/A | N/A | Yes
1.211 |  | Tocil Block - 9 ( Flats 49-54 ) | 2022-10-24 | TN-C-S | 3 Phase 4 wire | AC | 8 | 0.05 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 50 | N/A |  | Copper | 95 | Yes | Copper | 50 | Yes | Yes | N/A | N/A | N/A | N/A | Yes
1.238 |  | Tocil Block - 10 ( Flats 55-60 ) | 2022-10-25 | TN-S | 3 Phase 4 wire | AC | 4.4 | 0.11 | BS88 - 2 type Gm | 300 | 80 | Distributors facility | lim | ADS | BS 5419 | 200 | Copper | 240 | N/A |  | Steel | SWA | Yes | Copper | 25 | Yes | Yes | N/A | N/A | N/A | N/A | Yes
1.209 |  | Tocil Laundry | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | N/V | N/V | N/V | N/V | N/A |  | Steel | SWA | Yes | Copper | 25 | Yes | Yes | N/A | N/A | N/A | N/A | N/A
1.212 |  | Tocil Wardens House | 2022-10-26 | TN-C-S | 1 Phase 2 Wire | AC | 1.16 | 0.2 | BS1361 - Type 1 | 100 | 16.5 | Distributors facility | lim | ADS | BS EN 60947 - 3 | 100 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/V | N/A | N/A | N/A
2.01O |  | Transgenic Plants Laboratory | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | 2.52 | 0.14 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 250 | Copper | 95 | N/A |  | Steel | SWA | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | N/A | N/A
1.049 |  | University House | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 1250 | Copper | 2x185 | N/A |  | Copper | 185 | Yes | Copper | 50 | Yes | Yes | N/A | N/A | N/A | Yes | N/A
|  | University House Café Kitchen | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 400 | Copper | 185 | N/A |  | Copper | 185 | Yes | Copper | 50 | Yes | Yes | Yes | N/A | N/A | Yes | N/A
1.05O |  | University House Extension | 2022-10-26 | as 1.049 | [8 empty] | lim | ADS
1.078 |  | University House Plant Room | 2022-10-26 | as 1.049 | [8 empty] | lim | ADS
1.051 |  | University House Cycle Shed / Garages | 2022-10-26 | as 1.049 | [8 empty] | lim | ADS
1.003 |  | W.B.S. Café | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | 19.9 | 0.01 | BS EN 60947 - 2 ACB | 2000 | 65 | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 2000 | Copper | 3x500 | N/A |  | Copper | 500 | Yes | Copper | 95 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.003 |  | Warwick Business School | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | 19.9 | 0.01 | BS EN 60947 - 2 ACB | 2000 | 65 | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 2000 | Copper | 3x500 | N/A |  | Copper | 500 | Yes | Copper | 95 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.003 |  | Warwick Business School Phase 2 | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | 19.9 | 0.01 | BS EN 60947 - 2 ACB | 2000 | 65 | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 2000 | Copper | 3x500 | N/A |  | Copper | 500 | Yes | Copper | 95 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.004A |  | W.B.S. Teaching Centre | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | 16 | 0.08 | BS EN 60947 - 2 ACB | 2000 | 65 | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 1600 | Copper | bar | N/A |  | Copper | 120 | Yes | Copper | 50 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
3.015 |  | Westwood House | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | 2.88 | 0.19 | BS 88 - 2 type Gg | 100 | 80 | Distributors facility | lim | ADS | BS EN 60947 - 3 | 125 | Copper | 25 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
3.002 |  | Westwood Dining and Social Building | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | 2.38 | 0.19 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 400 | Copper | 500 | N/A |  | Steel | SWA | Yes | Copper | 16 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
|  | Westwood Refectory Kitchen (S+D) | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | 2.38 | 0.19 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 400 | Copper | 500 | N/A |  | Steel | SWA | Yes | Copper | 16 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
3.002 |  | Westwood I.T. Stores was Costa | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | 2.38 | 0.19 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 400 | Copper | 500 | N/A |  | Steel | SWA | Yes | Copper | 16 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
3.01O |  | Westwood I.T. Services | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | 12.63 | 0.03 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 400 | Copper | 300 | N/A |  | Steel | SWA | Yes | Copper | 25 | Yes | Yes | N/A | N/A | N/A | N/A | N/A
3.034 |  | Westwood Games Hall | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | 2.46 | 0.19 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 25 | N/A |  | Copper | 25 | Yes | Copper | 25 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
3.006 |  | Westwood Teaching Centre | 2022-10-26 | TN-C-S | 3 Phase 4 wire | AC | 6.34 | 0.08 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | N/V | Copper | 300 | N/A |  | Copper | 95 | Yes | Copper | 35 | Yes | N/V | Yes | Yes | N/A | Yes | N/A
3.012 |  | Westwood New Laundry | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | 1.19 | 0.42 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 200 | Copper | 50 | N/A |  | Copper | 35 | Yes | Copper | 35 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
3.074 |  | Westwood Storage Shed | 2022-10-26 | DUE | [8 empty] | lim | ADS
1.22O |  | Whitefield Flat No.1 | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | 1.73 | 0.23 | BS1361 - Type 1 | 100 | 16.5 | Distributors facility | lim | ADS | BS 5419 | 100 | Aluminium | 95 | N/A |  | Copper | 16 | Yes | Copper | 16 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.221 |  | Whitefield Flat No.2 | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | 2 | 0.2 | BS1361 - Type 1 | 100 | 16.5 | Distributors facility | lim | ADS | BS 5419 | 100 | Aluminium | 95 | N/A |  | Copper | 16 | Yes | Copper | 16 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.222 |  | Whitefield Flat No.3 | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | BS1361 - Type 1 | 100 | 16.5 | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 95 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.223 |  | Whitefield Flat No.4 | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 95 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.224 |  | Whitefield Flat No.5 | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 95 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.225 |  | Whitefield Flat No.6 | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 95 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.226 |  | Whitefield Flat No.7 | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 95 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.227 |  | Whitefield Flat No.8 | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 95 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.228 |  | Whitefield Flat No.9 | 2022-10-26 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 95 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.229 |  | Whitefield Flat No.10 | 2022-10-27 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 95 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.23O |  | Whitefield Flat No.11 | 2022-10-27 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 95 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.231 |  | Whitefield Flat No.12 | 2022-10-27 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 95 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.232 |  | Whitefield Flat No.13 | 2022-10-27 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 95 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.233 |  | Whitefield Flat No.14 | 2022-10-27 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 95 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.234 |  | Whitefield Flat No.15 | 2022-10-27 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 95 | N/A |  | Copper |  | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.235 |  | Whitefield Flat No.16 | 2022-10-27 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Copper | 95 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.236 |  | Whitefield Flat No.17 | 2022-10-27 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS 5419 | 100 | Aluminium | 95 | N/A |  | Copper | 16 | Yes | Copper | 10 | Yes | Yes | Yes | N/A | N/A | N/A | N/A
1.009 |  | Zeeman Building (Mathematics and Statistics | 2022-10-27 | TN-S | 3 Phase 4 wire | AC | 7.48 | 0.06 | BS EN 60947 - 2 ACB | 800 | 36 | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 2500 | Copper | 3x300 | N/A |  | Copper | 300 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
|  | Zeeman Building Plant Room | 2022-10-27 | TN-S | 3 Phase 4 wire | AC | 7.48 | 0.06 | BS EN 60947 - 2 ACB | 800 | 36 | Distributors facility | lim | ADS | BS EN 60947 - 2 ACB | 2500 | Copper | 3x300 | N/A |  | Copper | 300 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.338 |  | Footpath - Claycroft/Tocil | ? | [9 empty] | lim | ADS
1.339 |  | Footpath - By Rill | ? | [9 empty] | lim | ADS
2.03 |  | Footpath - Gibbet Hill | ? | [9 empty] | lim | ADS
1.34 |  | Footpath - Central Gibbet Hill | ? | [9 empty] | lim | ADS
1.341 |  | Footpath - Central Westwood | ? | [9 empty] | lim | ADS
1.342 |  | Footpath Lakeside/Heronbank | ? | [9 empty] | lim | ADS
1.343 |  | Footpath- Warwickshire Walk | ? | [9 empty] | lim | ADS
3.067 |  | Footpaths Westwood | ? | [9 empty] | lim | ADS
1.336 |  | Mathematical Science Building | 2022-10-27 | NEW BUILD | [8 empty] | lim | ADS
1.271 |  | Scarman Ho. Gardeners Store | 2022-10-27 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 2 MCCB | 1600 | Copper | 500 | N/A |  | Copper | 150 | Yes | Copper | 50 | Yes | Yes | Yes | Yes | N/A | Yes | N/A
1.049 |  | University House Comms. Room | 2022-10-27 | TN-S | 3 Phase 4 wire | AC | N/V | N/V | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 1250 | Copper | 2x185 | N/A |  | Copper | 185 | Yes | Copper | 50 | Yes | Yes | N/A | N/A | N/A | Yes | N/A
14.001 |  | Millenium Point Birmingham | 2022-10-27 | TN-S | 3 Phase 4 wire | AC | 5.21 | 0.08 | N/V | N/V | N/V | Distributors facility | lim | ADS | BS EN 60947 - 3 | 100 | Copper | 35 | N/A | LIM | Copper | LIM | Yes | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V | N/V

## Drop
Supply Charateristics & Earthing Arrangements | [7 empty] | Particulars of Installation Origin | [8 empty] | Earthing and Protective Bonding Conductors
Earthing Arrangement | Number of Live Conductors | Type | Prospective Fault Current - Ipf | External earth Fault impedance - Ze | Supply Protective Device BS EN | Rated Current | Short Circuit Capacity | Means of Earthing | Maximum Demand | Protective Measure | Main Switch- BS EN | Rating - A | Suuply Conductor Material | CSA | RCD Main Switch - !n | Measured Operating Time | Earthing Conductor Material | CSA | Continuity Verified | Main Protective Bonding Material | CSA | Continuity Verified | Water | Gas | Lightning | Oil | Structural Steelwork | Other Please State
TN-S | 1 Phase 2 Wire | AC |  |  | BS 88 - 2 type Gg | 30 |  | Distributors facility |  | ADS | BS 88 - 2 type Gg | 30 | Copper | 10 | 30mA |  | Copper | 10 | Yes | Copper | 10 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
TN-C-S | 3 Phase 4 wire | DC |  |  | BS88 - 2 type Gm | 32 |  | TX N - E link |  |  | BS88 - 2 type Gm | 32 | Aluminium | 16 | 100mA |  | Aluminium | 16 | Lim | Aluminium | 16 | Lim | Lim | Lim | Lim | Lim | Lim | Lim
TN-C |  |  |  |  | BS 3036 | 40 |  | LIM |  |  | BS 3036 | 40 | Steel | 25 | LIM |  | Steel | 25 | N/V | Steel | 25 | N/V | N/V | N/V | N/V | N/V | N/V | N/V
TT |  |  |  |  | BS1361 - Type 1 | 45 |  | N/A |  |  | BS1361 - Type 1 | 45 | LIM | 35 | N/A |  | LIM | 35 | N/A | N/V | 35 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[5 empty] | BS1361 - Type 2 | 50 |  |  |  |  | BS1361 - Type 2 | 50 | N/A | 50 |  |  | N/A | 50 |  | LIM | 50
[5 empty] | BS EN 60947 - 2 MCCB | 60 |  |  |  |  | BS EN 60947 - 2 MCCB | 60 |  | 95 |  |  |  | 95 |  | N/A | 95
[5 empty] | BS EN 60947 - 2 ACB | 63 |  |  |  |  | BS EN 60947 - 2 ACB | 63 |  | 120 |  |  |  | 120 |  |  | 120
[5 empty] | BS 5419 | 80 |  |  |  |  | BS 5419 | 80 |  | 150 |  |  |  | 150 |  |  | 150
[5 empty] | BS EN 60947 - 3 | 100 |  |  |  |  | BS EN 60947 - 3 | 100 |  | 185 |  |  |  | 185 |  |  | 185
[5 empty] | BS EN 60439 - 3 | 110 |  |  |  |  | BS EN 60439 - 3 | 110 |  | 240 |  |  |  | 240 |  |  | 240
[5 empty] | LIM | 125 |  |  |  |  | LIM | 125 |  | 300 |  |  |  | 300 |  |  | 300
[5 empty] | N/A | 150 |  |  |  |  | N/A | 150 |  | 400 |  |  |  | 400 |  |  | 400
[6 empty] | 175 |  |  |  |  | BS4752 | 175 |  | 500 |  |  |  | 500 |  |  | 500
[6 empty] | 200 |  |  |  |  | IEC 157-1 | 200 |  | 630 |  |  |  | 630 |  |  | 630
[6 empty] | 225 |  |  |  |  | MCCB Obsolete | 225 |  | 800 |  |  |  | 800 |  |  | 800
[6 empty] | 250 | [5 empty] | 250 |  | N/V |  |  |  | 185 x 2 |  |  | 95 x 2
[6 empty] | 300 | [5 empty] | 300 |  | LIM |  |  |  | 500 x 2 |  |  | LIM
[6 empty] | 350 | [5 empty] | 350 |  | 185 x 2 |  |  |  | 120 x 2 |  |  | N/V
[6 empty] | 400 | [5 empty] | 400 |  | 300 x 2 |  |  |  | Armour |  |  | 35 x 2
[6 empty] | 450 | [5 empty] | 450 |  | 70 |  |  |  | 147 Armour |  |  | N/A
[6 empty] | 500 | [5 empty] | 500 |  | 120 x 2 |  |  |  | 70
[6 empty] | 600 | [5 empty] | 600 |  | 50 x 4 |  |  |  | Tape 25 x 2.5
[6 empty] | 650 | [5 empty] | 650 |  | Busbar |  |  |  | LIM
[6 empty] | 700 | [5 empty] | 700 |  | 240 x 2 |  |  |  | N/A
[6 empty] | 750 | [5 empty] | 750 |  | 50 x 2 |  |  |  | MICC
[6 empty] | 800 | [5 empty] | 800 |  | 150 X 2 |  |  |  | 4
[6 empty] | 1000 | [5 empty] | 1000 |  | 2.5
[6 empty] | 2500 | [5 empty] | 1600 |  | 4
[6 empty] | LIM | [5 empty] | LIM
[6 empty] | N/A | [5 empty] | N/A
[6 empty] | 1600 | [5 empty] | 160
[6 empty] | 160 | [5 empty] | 3200
[6 empty] | 3200 | [5 empty] | 630
[6 empty] | 1250 | [5 empty] | 1125