To reset the Green break glass point boxes

If the box has been triggered the doors will not be locked and a thin yellow stripe will be visible at the top of the glass.

1. You will need the black plastic release key, in the Op’s key press

2. Insert the twin prong end into the holes in the underside of the unit

3. The single leg should be nearest you when inserting prongs

4. It should then be possible to remove the front from the unit

5. Remove key from unit

6. Replace front section by;

7. Push into slots about 2cm from top location

8. When located push upwards, this should move glass up into place and the door magnets re-energise

9. Check both doors are secure and return key to key press

